GUARANTEED TECHNICAL PARTICULARS OF 33 KV, 10 KN COMPOSITE POLYMER PIN INSULATORS

| Sl. No. | Description | Required Parameters | Offered Parameters |
| --- | --- | --- | --- |
| 1. | Name of Manufacturer |  |  |
| 2. | Address: |  |  |
|  | (a) registered Office |  |  |
|  | (b) Factory |  |  |
| 3. | Type of Insulators | 33KV,10 KN Composite Polymer Pin insulator |  |
| 4. | Standard specification to which the Insulators manufactured and tested | IEC-61109 with up to date amendments |  |
| 5. | Name of material used in manufacture of the Insulator (with class / grade) | Silicon Rubber |  |
| (a) | Material of core rod | ECR glass boron content free |  |
| (b) | Material of Housing & weather sheds (silicon content by weight) | Silicon Rubber 30% minimum |  |
| (c) | Material of end fittings | SGCI |  |
| (d) | Sealing compound for end fitting | RTV Silicon Sealant |  |
| 6. | Colour of Insulator | Grey |  |
| 7. | Electrical Characteristics: |  |  |
| (a) | Nominal system Voltage (KV rms) | 33 kv |  |
| (b) | Highest System Voltage (KV rms) | 36 kv |  |
| (c) | Dry power frequency withstand (KV rms) | 95 kv |  |
| (d) | Wet power frequency withstand (KV rms) | 75 kv |  |
| (e) | Dry flash over voltage (KV rms) | 130 kv |  |
| (f) | Wet flash over voltage (KV rms) | 90 kv |  |
| (g) | Dry lighting impulse withstand voltage |  |  |
|  | (a) Positive | 175 kv |  |
|  | (b) Negative | 175 kv |  |
| (h) | Dry lighting impulse flashover voltage |  |  |
|  | (a) Positive (KV peak) | 230 kv |  |
|  | (b) Negative (KV peak) | 230 kv |  |
| (i) | RIV at 1 MHz when energized at 30 kV (rms) under dry condition (microvolt) | <100 Micro Volt |  |
| (j) | Creepage distance (min) mm | 900 mm Minimum |  |
| 8. | Mechanical Characteristics: |  |  |
|  | Minimum failing load (KN) | 10 kN |  |
| 9. | Dimensions of Insulator: |  |  |
| i. | Weight (Kg.) | 2.2 Kg. (Min.) |  |
| ii. | Dia of FRP rod (mm) –Dia must be 33.5 mm (minimum) | 33.5 mm |  |
| iii. | Length of FRP rod (mm) | 340 mm (Min.) |  |
| iv. | Dia of weather sheds (mm) | Big – 106 mm & Small – 77 mm |  |
| v. | Thickness of housing (mm) | 3 mm |  |
| vi. | Dry arc distance (mm) | 325 mm |  |
| 10. | Dimensioned drawings of Insulator (including weight with tolerances in weight) enclosed. | Yes |  |
| 11. | Method of fixing of sheds to housing (specify ):- single mould or modular construction (injection moulding/compression moulding) | Injection Molding (Single Mould) |  |
| 12. | No. of weather sheds | 13 Nos. |  |
| 13. | Type of sheds |  |  |
|  | (i) Aerodynamic | Yes, Aerodynamic |  |
|  | (ii) With under ribs | Yes |  |
| 14. | Packing details |  |  |
|  | (a) Type of packing. | Gunny Bags |  |
|  | (b) No. of Insulators in each pack | 8 Nos. |  |
|  | (c ) Gross weight of package | 19 Kgs. Approx |  |
| 15. | Visible Discharge Test Voltage | 27 KV (RMS) |  |
| 16. | Any other particulars which the bidder may like to give. | Nil |  |

All parameters should be as per relevant IS/ISS & well suitable for MVVNL specification.

Note:

- In case of any contradiction in Technical Specification, the relevant IS or mentioned anywhere in tender documents; the parameter whichever is better, shall prevail.

- In case of any contradiction in terms & conditions mentioned at more than one place, the terms & conditions to the best advantage of MVVNL, will prevail.

PLACE:                                                                            SIGNATURE OF TENDERER NAME IN FULL

DATE                                                                                DESIGNATION/ STATUS IN THE FIRM

COMPANY SEAL

************************************************************************************